**Development Review Board (DRB)**

**Review Comments**

**Utility Development Section**

**Reviewer: Kristopher Cadena, P.E.**

**Phone: 505.289.3301**

|  |  |  |
| --- | --- | --- |
| **DRB Project No:**  **PR-2020-004030** | **Date:**  **08/26/20** | **Item No:**  **#6** |
| **Zone Atlas Page:**  **A-12 & A-13** | **Legal Description: A-12 & A-13**  **Location: GOLF COURSE RD NW between GOLF COURSE RD NW, BLACK ARROYO and WESTSIDE BLVD** | |
| **Request For:**  **SI-2020-00540 -** SITE PLAN | | |
|  | | |

**ABCWUA Comment:**

**Please provide written description of how the following comments were addressed with the next submittal.**

1. Serviceability Letter #200506 has been written and provides the conditions for service.
2. The property is outside of the Adopted Service Area. A Water Authority Board approved development agreement will be required prior to Site Plan approval. The serviceability letter will serve as an exhibit to the development agreement.

Response- received Water Authority Board approval on 9/23 item R-20-19 <https://abcwua.legistar.com/LegislationDetail.aspx?ID=4616928&GUID=75AD0FE0-9DB2-4BEE-B045-31BDD2CE5837> .

1. Utility Plan
   1. Previously, an 8” water meter was proposed for a single connection for a private onsite loop for both domestic and fire protection. Current proposal is a separate water service and fire line. The fire line as shown is going through the proposed large water meter vault which is not acceptable.

Response- fire line adjusted to avoid conflict with large water meter vault.