This appendix was prepared towards the development of a Drainage and Storm water Quality Master Plan for the South Broadway Area in general accordance with the requirements in the Scope of Work provided in the contract agreement between URS and the City of Albuquerque dated November 14, 2011. The information contained in this appendix was developed using existing drawings, reports, photographs, survey, and background information furnished by the City of Albuquerque and third parties. URS is neither responsible for, nor has confirmed the accuracy of this information. URS has relied on this information, as well as professional engineering judgment based on experience with similar projects, to develop this report. Additional investigations and analyses will be required for the future design phases of any drainage infrastructure within the limits of this study.

Appendix A

Existing Conditions 
Hydrologic Analysis

Table of Contents

A.1	Background	1

A.2	Watershed Delineation	1

A.3	Effects of Watersheds Outside Project Limits	5

A.4	Curve Number	6

A.5	Hydrologic Area Width	9

A.6	Percent Impervious	9

A.7	Estimation Of Rainfall	9

A.8	Assembly of Hydrologic Input to the SWMM	14

A.9	Model Results	15

A.10	References	20

List of Figures

Figure A.1: Project Location	2

Figure A.2: Watershed Delineation Map	3

Figure A.3: Land Use Map	7

Figure A.4: Hydrologic Soil Groups Map	8

Figure A.5: Cumulative 6-Hour Rainfall Distribution Comparison	11

Figure A.6: Cumulative 24-Hour Rainfall Distribution Comparison	12

Figure A.7: 24-Hour Incremental Depth Duration Curve	13

List of Tables

Table A.1: Bypass Flow	5

Table A.2: NOAA Atlas 14 Point Precipitation Depth (in.)	10

Table A.3: Hydrologic Model Results	15

Table A.4: Result Comparison	16

Table A.5: Total Watershed CN	18

Table A.6: CFS per Acre Comparison	19

Table A.7: 2-year 6-hour Rainfall Distribution	22

Table A.8: 2-year 24-hour Rainfall Distribution	23

Table A.9: 10-year 6-hour Rainfall Distribution	26

Table A.10: 10-year 24-hour Rainfall Distribution	27

Table A.11: 100-year 6-hour Rainfall Distribution	30

Table A.12: 100-year 24-hour Rainfall Distribution	31

Table A.13: SWMM Input Data	34

Table A.14: Offsite Drainage Potentially Impacting Project Area	35

List of Acronyms and Abbreviations

A	Area

AHYMO	Arid-lands Hydrologic Model

AMDS	Albuquerque Master Drainage Study

BN & SF	Burlington Northern & Santa Fe

cfs	Cubic Feet per Second

CN	Curve Number

COA	City of Albuquerque

DMP	Drainage Management Plan

EPA	United States Environmental Protection Agency

ft.	Foot or Feet

HSG	Hydrologic Soil Group

in.	inches

NMDOT	New Mexico Department of Transportation

NOAA	National Oceanic and Atmospheric Administration

NRCS	Natural Resources Conservation Service

Q	Flow (cfs)

SCS	Soil Conservation Service

SP&E	Specifications, Plans, and Estimates

sq. mi.	Square Mile

SSURGO	Soil Survey Geographic Database

SWMM	Storm Water Management Model

TR-55	Technical Release 55

USDA	United States Department of Agriculture

# Background

Under contract to the City of Albuquerque (COA), URS modeled the existing hydrologic conditions for the area affecting the South Broadway storm drain system. This system is bounded by Roma Avenue to the north, the city limit to the south (south of Woodward Road), Interstate-25 to the east, and the Burlington Northern & Santa Fe (BN & SF) Railroad to the west. This system will outlet into the San Jose Drain (SJD), which discharges to the Rio Grande. The hydrologic analysis consisted of the following steps:

- Delineating watershed boundaries

- Estimating each watershed curve number (CN)

- Determining each watershed’s average area slope

- Estimating the percent of impervious surface

- Determining the “width” of the watershed

- Estimating annual precipitation, and

- Developing the Storm Water Management Model (SWMM) to perform hydrologic calculations.

Detailed descriptions of the steps, assumptions, and results of the analysis are presented herein. An overview of the project area is provided on Figure A.1.

# Watershed Delineation

The South Broadway Sector Drainage Management Plan (DMP) [1], completed in 1990, was used as the basis of the watershed boundaries as requested by the COA. The watersheds for this study remained comparable to the original watersheds of the DMP as much as possible. Watersheds were modified to reflect either new storm drain lines or a change in the topography. Watershed delineation was also conducted on the area east of Interstate-25 in order to determine the amount of runoff affecting the system from outside the project limits. The watersheds were digitized using ArcView, version 9.3.1. All watersheds were delineated and modified using 2-foot contours generated from COA topography, and available orthophotography. Please refer to Figure A.2 for a map of the watersheds.

## Watershed Delineation – Within Project Limits

As previously stated, the watershed delineation and naming convention is based on the South Broadway Sector DMP [1]. Comparing the original watersheds with the available topography many watersheds maintained their original boundaries. Also, as in the original DMP analysis, watershed SJN – 750 was removed from the study. Watershed SJN – 750 drains directly to the South Diversion Channel and has no effect on the storm drain system of the area, which is why it is not included in this study.

Figure A.1: Project Location

Figure A.2: Watershed Delineation Map

While looking at the topography and available orthophotography many of the watersheds were adjusted. Some watersheds were adjusted to reflect the amount of runoff contributing to a specific storm drain. Other watersheds were adjusted to reflect new development. The modifications that were made based on storm drains were fairly minimal and did not alter the watershed beyond recognition of the original watershed. Watersheds that were changed to reflect development were altered significantly. The watersheds that underwent the most change are as follows:

- SJH – 109

- SJH – 202

- SJH – 700

- SJN – 710

- SJN – 720

- SJN – 730

- SJ – 2

- SJ – 3

- SJ – 4

### Watershed Modification

Three watersheds that underwent major modifications are SJH – 109, SJH – 202 and SJH – 700, primarily due to the development of the Broadway Industrial Center [2]. This industrial center has been under planning and development since 1997. The development changed the topography of the area and introduced a new storm drain. As a result SJH – 109 and SJH – 202 were reduced in size and SJH – 700 increased in size. Three significant detention basins were also created under the industrial center. To account for the additional detention basins, watershed SJH – 700 was divided into 4 different watersheds. The four watersheds that resulted are SJH – 700, SJH – 700A, SJH – 700B, and SJH – 700C.

Watersheds SJN – 710, SJN – 720 and SJN – 730 were also modified significantly; however, the changes are due to updated topographic data. The area does not have much development but the topographic data used was not comparable to the original watersheds of the area. These watersheds do not affect the South Broadway storm drain system because they are located at the south end of the project and surface flow to the SJD or down South Broadway Blvd. Due to the lack of effects these watersheds have on the storm drain system, the watershed difference were not investigated further.

Watersheds SJ – 2, SJ – 3 and SJ – 4 were modified to improve understanding of the storm drain system in this area. South of the pump station on Bell Street and Commercial Avenue the storm drain system becomes very intricate. While analyzing the area it became apparent that in order to produce alternatives for this area the watersheds had to be adjusted. The boundary between watershed SJ – 2 and SJ – 3 was modified, making SJ – 3 larger and SJ – 2 smaller. Watershed SJ – 4 was subdivided into SJ – 4A and SJ – 4B. The original watershed of SJ – 4 can still be compared to the two watersheds SJ – 4A and SJ – 4B by adding them together.

Though these watersheds no longer follow the original watershed boundaries of the 1990 DMP [1], these adjustments were necessary to reflect current conditions.

## Watershed Delineation – Outside Project Limits

Watersheds to the east of Interstate-25 were delineated to determine their effects on the project storm drain system. A few assumptions had to be made in line with the scope of work. These assumptions are as follows:

- The east boundary of the watershed is limited by the South Diversion Channel.

- If the South Diversion Channel does not intercept the potential watershed a very large interceptor storm drain will act as the east boundary. The drain runs from Roma Avenue south on Cedar Street to Silver Avenue where it turns west for a block to Mulberry Street and then it turns south. After making some directional changes the pipe ends up on Oak Street to outlet to the South Diversion Channel.

- The large interceptor storm drain will capture all the flow to the east with no bypass.

These watersheds were digitized using Arc View as well as using the 2- foot contours from the COA topography and available orthophotography. The naming convention of these watersheds is based on which “project watershed” they potentially effect. Numbering from north to south and lettering from west to east. The number and lettering system is separated from the particular watershed name by an underscore (e.g., SJH–100_1A). The numbering denotes the offsite watershed that could potentially affect the particular watershed. The lettering identifies the location of the watershed relative to Interstate-25.

Watersheds east of the large interceptor drain were delineated to ensure the interceptor drain will capture most of the flow from the east as assumed. This assumption will require more analysis to determine how much bypass will actually affect the South Broadway system. These watersheds have the letters B through D assigned to them.

# Effects of Watersheds Outside Project Limits

As stated above watersheds east of the large interceptor drain were delineated to determine the potential impact of the bypass flow from these watersheds on the project system. The Rational method was used to determine the peak runoff of these watersheds for the 100-year storm. The peak intensity and “c” coefficients for each watershed was determined using the COA DPM[3]. Table A.14 at the end of this analysis displays each watershed and the data used to determine the peak runoff. In order to calculate the bypass flow from each watershed the number of inlets within the watersheds was determined. Assuming each inlet is able to intake 4 cubic feet per second (cfs) this capacity was multiplied by the number of inlets per watershed, determining the potential maximum flow of the system. Assuming the inlet capacity is the limiting feature of the system the bypass flow was determined. Subtracting the watershed runoff from the potential max flow the amount of the bypass flow the inlets are able to catch was determined. Table A.1 displays the expected amount of bypass flow from each watershed.

Table A.1: Bypass Flow

| Watershed ID | Q100 (cfs) | # of Inlets per Basin | Inlet Intake (cfs) | Bypass Q (cfs) |
| --- | --- | --- | --- | --- |
| SJH-100_1B | 114 | 20 | 4 | 34 |
| SJH-100_3B | 167 | 34 | 4 | 31 |
| SJH-102_1B | 169 | 25 | 4 | 69 |
| SJH-102_1C | 529 | 53 | 4 | 317 |
| SJH-102_2B | 63 | 12 | 4 | 15 |
| SJH-102_2D | 151 | 4 | 4 | 135 |
| SJH-102_2C | 139 | 25 | 4 | 39 |
| SJH-105_1B | 151 | 19 | 4 | 75 |

The two watersheds which contribute the most bypass flow are SJH-102_1C and SJH-102_2D. The flow from SJH-102_1C will travel down Central Avenue. This flow could potentially impact the South Broadway system. The flow running down Central Avenue is expected to flow right through the project and continue west. The flow from SJH-102_2D is expected to travel down Lead Avenue or Coal Avenue and possibly pond in the park. It was determined that the potential impacts of the bypass flow from these watersheds are negligible; however, these watersheds require an in-depth study to determine impacts conclusively.

# Curve Number

Runoff losses were modeled using the SWMM. This was done by selecting “rainfall/runoff” in the process model section and “Curve Number” in the Infiltration model section, while setting up the model options. This infiltration process requires the user to input the CN, drying time, and conductivity of each watershed. The SWMM manual [4] indicates that the conductivity property has been deprecated and is no longer used; therefore the default number of 0.5 was not changed. Drying time is used to determine the minimum infiltration rate. This was set to 7 days which is reasonable to reflect the number of days it will take for a fully saturated soil to dry. Curve numbers were assigned based on the combination of hydrologic soil groups (HSGs) and land use cover described according to Technical Release 55: Urban Hydrology for Small Watersheds [5].

Land use types were estimated using available orthophotography and hand delineated in ArcMap. Polygons were completed with the land use cover attributed to each polygon. Figure 3 displays the land use types.

HSGs were determined by using the soil type shapefile for Bernalillo County available from the Soil Survey Geographic Database (SSURGO) [6]. The SSURGO soil shapefile delineates soil according to soil types, which were correlated to HSGs based on a key code also available from SSURGO. Soils were classified as Soil Group A, B, C, or D. Figure 4 displays the soil groups used for each watershed.

A CN shapefile was created by combining the land use and soils shapefile with the watersheds shapefile using the ArcMap Union tool. The CN shapefile contained the land use ID and soil type for each individual polygon created. Curve numbers were assigned to each polygon according to Technical Release -55 [5] using the land use/HSG combination. The area-weighted average CN for each watershed was then calculated using the following equation: CNavg = Σ (Area*CN) / Σ (area sum).

Figure A.3: Land Use Map

Figure A.4: Hydrologic Soil Groups Map

# Hydrologic Area Width

As routing for each watersheds pervious area, SWMM only requires the area-weighted average width and slope be inputs for calculation. The area width takes into account the overland flow path length for each pervious land type within the watershed. This was calculated by applying the following equation:

Wavg = (PA1/WA1)*L1 + (PA2/WA2)*L2

Where: 	Wavg = area-weighted average width

PA = pervious area (ft2)

WA = watershed area (ft2)

L = overland flow length (ft)

The overland flow path length was determined using ArcMap and available orthophotography. The area-weighted average slope was calculated using the same equation only applying the slope of each pervious area within the watershed. The equation used is as follows:

Savg = (PA1/WA1)*s1 + (PA2/WA2)*s2

Where: 	Savg = area-weighted average slope (%)

PA = pervious area (ft2)

WA = watershed area (ft2)

s = pervious area slope (%)

The slope of the representative pervious areas was determined using ArcMap while using the 2-foot contour data from the COA topography and applying the overland flow length of the particular pervious type.

# Percent Impervious

The percent impervious was calculated for each watershed. The SWMM manual [4] describes the impervious area as the area which is impervious and drains directly to a storm water conveyance system such as a gutter, pipe, swale, etc. To be consistent among watersheds the road/street system is considered the impervious area. Parking lots and other impervious areas that are not typically considered roads are taken into consideration while calculating the CN of the block within the watershed. The percent impervious was calculated by taking the area of the impervious sections of the watershed and dividing by the total watershed area.

# Estimation Of Rainfall

Precipitation was initially estimated by assuming a Soil Conservation Service (SCS) 24-hour Type II-75 rainfall distribution. The total rainfall depths, summarized in Table A.2 below, were applied to the SCS Type II-75 rainfall distribution in order to develop a rainfall distribution for input into the SWMM.

Table A.2: NOAA Atlas 14 Point Precipitation Depth (in.)

| Duration | Average Recurrence Interval (Years) |  |  |
| --- | --- | --- | --- |
|  | 2 | 10 | 100 |
| 6-hour | 0.97 | 1.47 | 2.23 |
| 24-hour | 1.23 | 1.77 | 2.60 |

To be consistent with the COA DPM [1] a 6-hour rainfall distribution was developed for the analysis. The COA requires the design of storm drain systems to be able to convey the 6-hour storm. The New Mexico Department of Transportation (NMDOT) Drainage Manual Volume 1: Hydrology [7], was used to create the 6-hour distribution, with the peak intensity at 1.5 hours. Placing the peak intensity at 1.5 hours was based on the 24-hour storm placing the peak at 6-hours. The 24-hour storm has a peak intensity occur at a quarter of the total storm duration; therefore applying the peak intensity at a quarter of the 6-hour storm places the peak intensity at 1.5 hours. The 100-year, 6-hour storm distribution created using the NMDOT procedure was compared to the Arid Lands Hydrology Model (AHYMO). In AHYMO the comparable rainfall type is identified as “rainfall Type 1.” According to the user manual, a rainfall Type 1 is the 6-hour rainfall distribution based on the National Oceanic and Atmospheric Administration (NOAA) Atlas 14 with peak intensity at 1.4 hours. Figure A.5: Cumulative 6-Hour Rainfall Distribution Comparison shows the distributions are very similar; therefore, the NMDOT distribution will be used for modeling purposes.

In order to keep the rainfall distributions consistent, the 24-hour storm distribution was also created using the NMDOT Drainage Manual. The rainfall distribution created was then compared to the AHYMO rainfall distribution. AHYMO refers to the 24-hour rainfall distribution as “rainfall Type 5,” which is the 24-hour SCS Type II-75 distribution for New Mexico with peak intensity at 6-hours. Figure A.6: Cumulative 24-Hour Rainfall Distribution Comparison displays the rainfall distributions; they are also very close by comparison as well.

As a result, for consistent methodology as well as for a better representation of the runoff occurring in the area, the NMDOT rainfall distribution was used. The NOAA Atlas 14 total rainfall depth in conjunction with the NMDOT rainfall distribution became input into the SWMM. This was done for both the 24-hour and 6-hour storm durations. Cumulative depth and incremental depths are very similar, but with a difference in the peak. Figure A.7 displays the incremental depth curve of the 24-hour storm and as can be seen the two model peaks are not the same. As a result the runoff within the project area becomes a better representation of the runoff of the area. Tables A.7 through A.12  show the rainfall distribution for the 2-year, 24-hour storm; 2-year, 6-hour storm; 10-year, 24-hour storm; 10-year, 6-hour storm; 100-year, 24-hour storm; and 100-year, 6-hour storm.

Figure A.5: Cumulative 6-Hour Rainfall Distribution Comparison

Figure A.6: Cumulative 24-Hour Rainfall Distribution Comparison

Figure A.7: 24-Hour Incremental Depth Duration Curve

# Assembly of Hydrologic Input to the SWMM

Hydrologic elements were created for each watershed within the study area. Each element required the following input data as a representation of the actual watershed being modeled.

- Name – The name of the watershed being analyzed.

- Rain Gage – The rainfall distribution used as previously discussed.

- Outlet – The point in which the calculated flow of the watershed enters the hydraulic system of the model.

- Area – Total area of the watershed.

- Width – The characteristic of the overland flow path for sheet flow runoff, as previously described.

- % Slope – The average percent slope of the watershed, as previously described.

- % Impervious – The percent of land area that is impervious within the watershed, which has been identified in this analysis as the streets.

- N-Impervious – Manning’s “n” of the overland flow over an impervious area. To be consistent within watersheds all N values were designated as 0.018, which is consistent with the COA DMP guidelines.

- N-Pervious – Manning’s “n” of the overland flow over a pervious area. To be consistent within watersheds all N values were designated as 0.060 to account for major objects disturbing the flow path.

- D Store-Impervious – Depth of depression storage on the impervious area of the watershed. The user manual suggests a range of 0.05 - 0.10 inches. Due to the lack of storage expected on the streets, a value of 0.05 inches was used on all watersheds.

- D Store-Pervious – Depth of depression storage on the pervious areas of the watershed. The user manual suggests a range of 0.10 – 0.20 inches for lawns, and 0.20 inches for pastures. A value of 0.12 inches was used on all watersheds.

- % Zero-Impervious – The percent of impervious area with no depression storage. The default of 25% was used. It is expected that 25% of the runoff will not be affected by ponding, and will flow directly to the hydraulic element of the model.

- Subarea Routing – The internal routing of runoff between pervious and impervious areas. Impervious was used in this study. The impervious selection indicates that runoff from pervious areas will flow to impervious areas before draining to a storm water conveyance system.

- Percent Routed – Indicates the percent of runoff routed between the pervious/impervious areas. One hundred percent (100%) was used in this study.

- Infiltration – Indicates the method used to determine infiltration. The CN method was used as previously described.

Other input data not previously discussed has not been used or is irrelevant to the watershed modeling process. Table A.13 displays the SWMM input data for each watershed.

# Model Results

Model results for each watershed can be found in the table below.

Table A.3: Hydrologic Model Results

| Watershed ID | Area (sq. mi.) | Peak Runoff 100-year, 24-hour Storm (cfs) | Peak Runoff 100-year, 6-hour Storm (cfs) |
| --- | --- | --- | --- |
| BH-134 | 0.054 | 106 | 96 |
| SJH-100 | 0.083 | 175 | 163 |
| SJH-102 | 0.165 | 264 | 236 |
| SJH-105 | 0.081 | 124 | 109 |
| SJH-106 | 0.089 | 130 | 114 |
| SJH-150 | 0.073 | 117 | 104 |
| SJH-152 | 0.127 | 166 | 142 |
| SJH-153 | 0.065 | 97 | 86 |
| SJH-200 | 0.047 | 70 | 62 |
| SJH-202 | 0.064 | 71 | 58 |
| SJH-700 | 0.034 | 46 | 39 |
| SJH-109 | 0.099 | 107 | 89 |
| SJN-710 | 0.012 | 11 | 9 |
| SJN-720 | 0.026 | 27 | 22 |
| SJN-730 | 0.049 | 51 | 42 |
| SJN-740 | 0.129 | 99 | 88 |
| SJ-8 | 0.045 | 70 | 62 |
| SJ-90L | 0.046 | 33 | 29 |
| SJ-955 | 0.045 | 46 | 38 |
| SJ-7 | 0.073 | 70 | 58 |
| SJH-701 | 0.067 | 69 | 56 |
| SJ-5 | 0.054 | 72 | 61 |
| SJ-4A&B* | 0.074 | 86 | 72 |
| SJ-4A | 0.040 | 52 | 44 |
| SJ-4B | 0.034 | 34 | 28 |
| SJ-3 | 0.047 | 80 | 71 |
| SJ-2 | 0.073 | 86 | 72 |
| SJ-1 | 0.075 | 103 | 88 |
| SJN-10 | 0.016 | 15 | 12 |
| SJN-6 | 0.044 | 49 | 41 |

*Combination of SJ – 4A and SJ – 4B

While looking at the results and comparing them to the previous South Broadway DMP [1] it became apparent that the peak runoffs of the two studies are quite different. A comparison of the inputs and outputs of the two studies is displayed in Table A.4.

Table A.4: Result Comparison

| Watershed ID | Current SWMM Model |  |  |  |  | S. Broadway DMP |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Area (sq. mi.) | Input CN | Watershed CN | Slope (ft/ft) | Peak Q (cfs) | Area (sq. mi.) | Input CN | Watershed CN | Slope (ft/ft) | Peak Q (cfs) |
| BH-134 | 0.054 | 88 | 89 | 0.026 | 106 | 0.066 | 54 | 83 | 0.055 | 180 |
| SJH-100* | 0.083 | 87 | 90 | 0.028 | 175 | 0.097 | 54 | 80 |  | 210 |
| SJH-102* | 0.165 | 79 | 83 | 0.030 | 264 | 0.175 | 54 | 72 |  | 215 |
| SJH-105* | 0.081 | 79 | 82 | 0.027 | 124 | 0.071 | 54 | 69 |  | 103 |
| SJH-106* | 0.089 | 77 | 80 | 0.028 | 130 | 0.095 | 54 | 69 |  | 117 |
| SJH-150* | 0.073 | 79 | 83 | 0.026 | 117 | 0.075 | 54 | 69 |  | 126 |
| SJH-152* | 0.127 | 77 | 80 | 0.028 | 166 | 0.132 | 54 | 69 |  | 194 |
| SJH-153* | 0.065 | 77 | 80 | 0.032 | 97 | 0.062 | 54 | 72 |  | 108 |
| SJH-200* | 0.047 | 81 | 84 | 0.019 | 70 | 0.055 | 54 | 72 |  | 94 |
| SJH-202* | 0.064 | 79 | 80 | 0.025 | 71 | 0.082 | 54 | 58 |  | 28 |
| SJH-700* | 0.034 | 82 | 83 | 0.017 | 46 | 0.056 | 69 | 69 |  | 33 |
| SJH-109 | 0.099 | 73 | 74 | 0.053 | 107 | 0.104 | 70 | 72 | 0.024 | 65 |
| SJN-710 | 0.012 | 70 | 74 | 0.027 | 11 | 0.032 | 69 | 70 | 0.037 | 21 |
| SJN-720 | 0.026 | 71 | 71 | 0.048 | 27 | 0.040 | 69 | 70 | 0.026 | 20 |
| SJN-730 | 0.049 | 74 | 74 | 0.035 | 51 | 0.042 | 62 | 76 | 0.028 | 96 |
| SJN-740 | 0.129 | 88 | 88 | 0.004 | 99 | 0.130 | 70 | 81 | 0.002 | 130 |
| SJ-8 | 0.045 | 82 | 84 | 0.013 | 70 | 0.046 | 78 | 82 | 0.018 | 99 |
| SJ-90L | 0.046 | 88 | 88 | 0.003 | 33 | 0.050 | 79 | 86 | 0.002 | 54 |
| SJ-955 | 0.045 | 76 | 78 | 0.010 | 46 | 0.041 | 79 | 86 | 0.002 | 58 |
| SJ-7 | 0.073 | 70 | 73 | 0.019 | 70 | 0.068 | 65 | 76 | 0.008 | 70 |
| SJH-701 | 0.067 | 77 | 78 | 0.021 | 69 | 0.078 | 69 | 78 | 0.010 | 96 |
| SJ-5 | 0.054 | 79 | 81 | 0.022 | 72 | 0.041 | 62 | 76 | 0.007 | 48 |
| SJ-4A&B** | 0.074 | 76 | 78 | 0.015 | 86 | 0.188 | 66 | 77 | 0.007 | 105 |
| SJ-4A | 0.040 | 78 |  | 0.016 | 52 |  |  |  |  |  |
| SJ-4B | 0.034 | 74 |  | 0.015 | 34 |  |  |  |  |  |
| SJ-3 | 0.047 | 82 | 85 | 0.021 | 80 | 0.023 | 64 | 76 | 0.012 | 41 |
| SJ-2 | 0.073 | 76 | 79 | 0.017 | 86 | 0.098 | 65 | 77 | 0.004 | 88 |
| SJ-1 | 0.075 | 84 | 85 | 0.020 | 103 | 0.079 | 60 | 71 | 0.005 | 48 |
| SJN-10 | 0.016 | 76 | 77 | 0.012 | 15 | 0.016 | 79 | 83 | 0.000 | 12 |
| SJN-6 | 0.044 | 76 | 79 | 0.011 | 49 | 0.052 | 70 | 78 | 0.001 | 26 |

*Basins which the S. Broadway DMP used all data except % impervious from Original AMDS report

** Combination of SJ – 4A and SJ – 4B

Table A.4 shows the difference in peak runoff between the current SWMM model and the previous South Broadway DMP [1]. There are many factors which resulted in these differences. For example, certain parameters have changed since the 1990 DMP, such as the rainfall data used to determine the areas hyetograph. The South Broadway DMP[1] used NOAA Atlas 2 and the current model used NOAA Atlas 14. The CN is another factor that affects peak runoff. The column titled “Input CN” is the CN that was determined using ArcMap and calculated for the pervious areas of each watershed. The column titled “Watershed CN” is the result of combining the pervious area CN with the impervious area. This combination provides a total watershed CN rather than just a pervious area CN. The total watershed CN was determined using the following equation:

CNtotal = (IA*98+ PA*CNp) / A

Where:		CNtotal = total watershed CN

IA = impervious area (sq. mi.)

98 = TR-55 CN for impervious area

PA = pervious area (sq. mi.)

CNp = CN of the pervious area (determined as input data)

A = total area of watershed (sq. mi.)

Table A.5 displays the values used to determine the total watershed CN as well as the results and comparison.

As can be seen in Table A.5, the watersheds that have a large difference in CN are those that have not been updated since the Albuquerque Master Drainage Study (AMDS) report [8]. All other watersheds have comparable CNs, which makes sense and is reasonable. The comparison of data inputs has not been able to explain the differences in peak Qs between the two different studies. With that said, a comparison of the peak Q per acre was also calculated. Table A.6 presents the results of a peak runoff per acre comparison.

The peak runoff per acre indicates how similar each study’s results are. As can be seen the current SWMM model has an average runoff per acre of 2.1 cfs/acre and the South Broadway DMP [1] has an average runoff per acre of 1.8 cfs/acre. This comparison confirms that the current SWMM model results are reasonable and acceptable. It can also be seen that the standard deviation of the current model is less than the previous study. This means that the current model results are closer in relation to each other than those of the previous model, where there was more variation between watershed runoff.

Table A.5: Total Watershed CN

| Watershed ID | Current SWMM Model |  |  |  |  |  | S. Broadway DMP |  |  |  |  |  | Δ CN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Area (sq.mi.) | % Imperv. | Imperv. Area (sq.mi.) | Perv. Area (sq.mi.) | Perv. Area CN | Total CN | Area (sq.mi.) | % Imperv. | Imperv. Area (sq.mi.) | Perv. Area (sq.mi.) | Perv. Area CN | Total CN |  |
| BH-134 | 0.053 | 10 | 0.0054 | 0.048 | 88 | 89 | 0.066 | 65 | 0.0429 | 0.023 | 54 | 83 | 6 |
| SJH-100* | 0.083 | 23 | 0.0191 | 0.064 | 87 | 90 | 0.097 | 60 | 0.0582 | 0.038 | 54 | 80 | 9 |
| SJH-102* | 0.165 | 21 | 0.0347 | 0.130 | 79 | 83 | 0.175 | 40 | 0.0700 | 0.105 | 54 | 72 | 11 |
| SJH-105* | 0.081 | 17 | 0.0138 | 0.067 | 79 | 82 | 0.071 | 35 | 0.0249 | 0.046 | 54 | 69 | 13 |
| SJH-106* | 0.089 | 16 | 0.0143 | 0.075 | 77 | 80 | 0.095 | 35 | 0.0333 | 0.061 | 54 | 69 | 11 |
| SJH-150* | 0.073 | 21 | 0.0153 | 0.057 | 79 | 83 | 0.075 | 35 | 0.0263 | 0.048 | 54 | 69 | 14 |
| SJH-152* | 0.126 | 14 | 0.0177 | 0.109 | 77 | 80 | 0.132 | 35 | 0.0462 | 0.085 | 54 | 69 | 11 |
| SJH-153* | 0.065 | 16 | 0.0105 | 0.054 | 77 | 80 | 0.062 | 40 | 0.0248 | 0.037 | 54 | 72 | 9 |
| SJH-200* | 0.047 | 20 | 0.0095 | 0.037 | 81 | 84 | 0.055 | 40 | 0.0220 | 0.033 | 54 | 72 | 13 |
| SJH-202* | 0.063 | 6 | 0.0038 | 0.060 | 79 | 80 | 0.082 | 10 | 0.0082 | 0.073 | 54 | 58 | 22 |
| SJH-700* | 0.033 | 7 | 0.0024 | 0.031 | 82 | 83 | 0.056 | 0 | 0.0000 | 0.056 | 69 | 69 | 14 |
| SJH-109 | 0.099 | 5 | 0.0050 | 0.094 | 73 | 74 | 0.104 | 8 | 0.0083 | 0.095 | 70 | 72 | 2 |
| SJN-710 | 0.012 | 13 | 0.0016 | 0.010 | 70 | 74 | 0.032 | 4 | 0.0013 | 0.030 | 69 | 70 | 3 |
| SJN-720 | 0.025 | 0 | 0.0000 | 0.025 | 71 | 71 | 0.040 | 2 | 0.0008 | 0.040 | 69 | 70 | 1 |
| SJN-730 | 0.048 | 0 | 0.0000 | 0.048 | 74 | 74 | 0.042 | 40 | 0.0169 | 0.025 | 62 | 76 | -2 |
| SJN-740 | 0.129 | 0 | 0.0000 | 0.129 | 88 | 88 | 0.130 | 40 | 0.0521 | 0.078 | 70 | 81 | 7 |
| SJ-8 | 0.044 | 14 | 0.0062 | 0.038 | 82 | 84 | 0.046 | 20 | 0.0092 | 0.036 | 78 | 82 | 2 |
| SJ-90L | 0.045 | 2 | 0.0009 | 0.044 | 88 | 88 | 0.050 | 35 | 0.0176 | 0.032 | 79 | 86 | 3 |
| SJ-955 | 0.044 | 11 | 0.0049 | 0.039 | 76 | 78 | 0.041 | 35 | 0.0147 | 0.027 | 79 | 86 | -7 |
| SJ-7 | 0.072 | 12 | 0.0087 | 0.064 | 70 | 73 | 0.068 | 32 | 0.0219 | 0.046 | 65 | 76 | -2 |
| SJH-701 | 0.067 | 3 | 0.0020 | 0.065 | 77 | 78 | 0.078 | 30 | 0.0236 | 0.055 | 69 | 78 | 0 |
| SJ-5 | 0.054 | 11 | 0.0059 | 0.048 | 79 | 81 | 0.041 | 40 | 0.0166 | 0.024 | 62 | 76 | 5 |
| SJ-4A&B | 0.074 | 8.5 | 0.0063 | 0.068 | 76 | 78 | 0.188 | 35 | 0.0658 | 0.122 | 66 | 77 | 1 |
| SJ-3 | 0.047 | 19 | 0.0090 | 0.038 | 82 | 85 | 0.023 | 35 | 0.0083 | 0.015 | 64 | 76 | 9 |
| SJ-2 | 0.073 | 12 | 0.0088 | 0.064 | 76 | 79 | 0.098 | 35 | 0.0346 | 0.064 | 65 | 77 | 2 |
| SJ-1 | 0.075 | 4 | 0.0030 | 0.072 | 84 | 85 | 0.079 | 30 | 0.0239 | 0.055 | 60 | 71 | 13 |
| SJN-10 | 0.016 | 3 | 0.0005 | 0.015 | 76 | 77 | 0.016 | 20 | 0.0033 | 0.013 | 79 | 83 | -6 |
| SJN-6 | 0.044 | 13 | 0.0057 | 0.038 | 76 | 79 | 0.052 | 30 | 0.0158 | 0.036 | 70 | 78 | 0 |

*Basins which the S. Broadway DMP used all data except % impervious from Original AMDS report

Table A.6: CFS per Acre Comparison

| Watershed | Current SWMM Model |  |  |  | S. Broadway DMP 1990 |  |  |  | Δ cfs/acre |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Area (sq.mi.) | Area (acre) | Peak Q (cfs) | Peak Q / Acre | Area (sq.mi.) | Area (acre) | Peak Q (cfs) | Peak Q / Acre |  |
| BH-134 | 0.05 | 34.30 | 105.7 | 3.1 | 0.066 | 42.24 | 180 | 4.3 | -1.2 |
| SJH-100 | 0.08 | 53.25 | 175.0 | 3.3 | 0.097 | 62.08 | 210 | 3.4 | -0.1 |
| SJH-102 | 0.17 | 105.79 | 264.1 | 2.5 | 0.175 | 112.00 | 215 | 1.9 | 0.6 |
| SJH-105 | 0.08 | 52.03 | 123.9 | 2.4 | 0.071 | 45.44 | 103 | 2.3 | 0.1 |
| SJH-106 | 0.09 | 57.15 | 130.2 | 2.3 | 0.095 | 60.80 | 117 | 1.9 | 0.4 |
| SJH-150 | 0.07 | 46.72 | 116.7 | 2.5 | 0.075 | 48.00 | 126 | 2.6 | -0.1 |
| SJH-152 | 0.13 | 81.09 | 165.7 | 2.0 | 0.132 | 84.48 | 194 | 2.3 | -0.3 |
| SJH-153 | 0.07 | 41.86 | 97.4 | 2.3 | 0.062 | 39.68 | 108 | 2.7 | -0.4 |
| SJH-200 | 0.05 | 30.34 | 70.3 | 2.3 | 0.055 | 35.20 | 94 | 2.7 | -0.4 |
| SJH-202 | 0.06 | 40.83 | 71.1 | 1.7 | 0.082 | 52.48 | 28 | 0.5 | 1.2 |
| SJH-700 | 0.03 | 21.63 | 45.7 | 2.1 | 0.057 | 36.16 | 33 | 0.9 | 1.2 |
| SJH-109 | 0.10 | 63.42 | 106.9 | 1.7 | 0.104 | 66.69 | 65 | 1.0 | 0.7 |
| SJN-710 | 0.01 | 7.94 | 11.2 | 1.4 | 0.032 | 20.54 | 21 | 1.0 | 0.4 |
| SJN-720 | 0.03 | 16.58 | 26.6 | 1.6 | 0.041 | 26.18 | 20 | 0.8 | 0.8 |
| SJN-730 | 0.05 | 31.17 | 51.4 | 1.6 | 0.042 | 27.07 | 96 | 3.5 | -1.9 |
| SJN-740 | 0.13 | 82.82 | 99.4 | 1.2 | 0.130 | 83.33 | 130 | 1.6 | -0.4 |
| SJ-8 | 0.04 | 28.48 | 70.1 | 2.5 | 0.046 | 29.44 | 99 | 3.4 | -0.9 |
| SJ-90L | 0.05 | 29.25 | 33.1 | 1.1 | 0.050 | 32.26 | 54 | 1.7 | -0.5 |
| SJ-955 | 0.04 | 28.61 | 46.1 | 1.6 | 0.042 | 26.82 | 58 | 2.2 | -0.6 |
| SJ-7 | 0.07 | 46.59 | 70.4 | 1.5 | 0.068 | 43.78 | 70 | 1.6 | -0.1 |
| SJH-701 | 0.07 | 43.14 | 68.8 | 1.6 | 0.079 | 50.43 | 96 | 1.9 | -0.3 |
| SJ-5 | 0.05 | 34.56 | 71.8 | 2.1 | 0.041 | 26.50 | 48 | 1.8 | 0.3 |
| SJ-4A&B* | 0.07 | 47.62 | 86.3 | 1.8 | 0.188 | 120.38 | 105 | 0.9 | 0.9 |
| SJ-3 | 0.05 | 30.21 | 80.0 | 2.6 | 0.024 | 15.17 | 41 | 2.7 | -0.1 |
| SJ-2 | 0.07 | 46.91 | 85.7 | 1.8 | 0.099 | 63.30 | 88 | 1.4 | 0.4 |
| SJ-1 | 0.08 | 48.13 | 103.2 | 2.1 | 0.080 | 50.88 | 48 | 0.9 | 1.2 |
| SJN-10 | 0.02 | 10.43 | 15.0 | 1.4 | 0.017 | 10.69 | 12 | 1.1 | 0.3 |
| SJN-6 | 0.04 | 28.22 | 48.6 | 1.7 | 0.053 | 33.66 | 26 | 0.8 | 0.9 |
| Statistics of Peak Q / Acre |  |  |  |  |  |  |  |  |  |
| Average (cfs/acre) |  |  |  | 2.1 |  |  |  | 1.8 |  |
| Standard Deviation |  |  |  | 0.53 |  |  |  | 0.97 |  |

*Combination of SJ – 4A and SJ – 4B

# References

1.	Bohannan-Huston, Inc. 1990. South Broadway Sector Drainage Management Plan.

2.	D. Mark Goodwin & Associates. 1997. Drainage Report for Broadway Industrial Center.

3.	City of Albuquerque, 2008, Albuquerque, New Mexico Development Process Manual. American Legal Publishing Corp.

4.	United States Environmental Protection Agency (EPA). 2010. Storm Water Management Model User’s Manual, Version 5.0.

5.	USDA NRCS. 1986. Urban Hydrology for Small Watersheds TR-55.

6.	USDA National Resource Conservation Commission (NRCS). 2008. Soil Survey Geographic Database (SSURGO) Soil Data for Bernalillo County and Parts of Sandoval and Valencia Counties, New Mexico.

7.	NMDOT Preliminary Design Bureau/Drainage Section. 1995. Drainage Manual Volume 1, Hydrology.

8.	Bohannan-Huston, Inc. 1981. Albuquerque Master Drainage Study.

Tables

Hydrologic Data

Table A.7: 2-year 6-hour Rainfall Distribution

Table A.8: 2-year 24-hour Rainfall Distribution

K

Table A.9: 10-year 6-hour Rainfall Distribution

Table A.10: 10-year 24-hour Rainfall Distribution

Table A.11: 100-year 6-hour Rainfall Distribution

Table A.12: 100-year 24-hour Rainfall Distribution

Table A.13: SWMM Input Data

Table A.14: Offsite Drainage Potentially Impacting Project Area