## Det Rout Summary
Table 2
Detention Pond Routing Summary
(EXISTING Conditions, DEVEX Conditions and ULTIMATE Conditions)
Detention Pond Name | Existing or Proposed Pond | Development / Model Condition | Model Analysis Point Name | Return Period (24-hour duration storm) | Drainage Area | Storm Return Period (100-yr. 24-hr. duration) | Peak Inflow | Peak Outflow | Inflow Runoff Volume | Outflow Runoff Volume | Maximum Storage Volume (top of embank ment) | Peak Storage Volume | Peak Storage Volume | Peak Water Surface Elevation | Top of Principal Spillway Elevation | Emergency Spillway Elevation | Pond Invert Elevation | Max Pond Depth | Water Depth | Top of Pond Embankment Elevation | Freeboard to Principal Spillway Elevation | Freeboard to Emergency Spillway Elevation | Freeboard to top of Pond Embankment
|  |  |  | year | sq mi |  | cfs | cfs | ac-ft | ac-ft | ac-ft | ac-ft | ac-ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft
a | a | b | a |  |  |  | c | c | c | c | d | c | c | c | d | d | d | d |  | d | e | e | e
Existing Detention Facilities
Sunset | Existing | EXISTING |  | 100 | 0.2558 |  | 297 | 35 | 15.1475 | 15.147 | 25.5 |  | 9.2063 | 5617.06 | 5616.73 | 5620 | 5606 | 16 | 11.06 | 5622 | -0.33 | 2.94 | 4.94
" " | " " | DEVEX / ULTIMATE |  | 100 | 0.2558 |  | 349 | 37 | 20.3148 | 20.3244 | 25.5 |  | 11.8589 | 5618.35 | 5616.73 | 5620 | 5606 | 16 | 12.35 | 5622 | -1.62 | 1.65 | 3.65
Wallen Subdivision | Existing | EXISTING |  | 100 | 0.0154 |  | 19 | 1 | 0.569 | 0.568 | 5.8267 |  | 0.4589 | 5657.12 | 5655.88 | 5660 | 5655.88 | 9.12 | 1.24 | 5665 | -1.24 | 2.88 | 7.88
" " | " " | DEVEX / ULTIMATE |  | 100 | 0.0154 |  | 32 | 2 | 1.3603 | 1.3537 | 5.8267 |  | 0.9634 | 5658.41 | 5655.88 | 5660 | 5655.88 | 9.12 | 2.53 | 5665 | -2.53 | 1.59 | 6.59
Sugar Ridge Subdivision | Existing | EXISTING |  | 100 | 0.196 |  | 105 | 94 | 5.1478 | 4.6488 | 2.6759 |  | 1.234 | 5567.36 | 5561.13 | 5567.26 | 5560 | 11 | 7.36 | 5571 | -6.23 | -0.1 | 3.64
" " | " " | DEVEX |  | 100 | 0.196 |  | 131 | 120 | 5.2215 | 4.7223 | 2.6759 |  | 1.3191 | 5567.61 | 5561.13 | 5567.26 | 5560 | 11 | 7.61 | 5571 | -6.48 | -0.35 | 3.39
" " | " " | ULTIMATE |  | 100 | 0.196 |  | 106 | 92 | 4.9542 | 4.4549 | 2.6759 |  | 1.2319 | 5567.35 | 5561.13 | 5567.26 | 5560 | 11 | 7.35 | 5571 | -6.22 | -0.09 | 3.65
Wexford Pond [A] | Existing | EXISTING |  | 100 | 0.2326 |  | 368 | 135 | 27.7897 | 27.7879 | 12.5 |  | 9.2655 | 40.04 | 31.5 | 40 | 31.5 | 10 | 8.54 | 41.5 | -8.54 | -0.04 | 1.46
" " | " " | DEVEX / ULTIMATE |  | 100 | 0.2326 |  | 368 | 135 | 27.6672 | 27.6653 | 12.5 |  | 9.2614 | 40.03 | 31.5 | 40 | 31.5 | 10 | 8.53 | 41.5 | -8.53 | -0.03 | 1.47
Gateway | Existing | EXISTING |  | 100 | 0.4724 |  | 503 | 265 | 19.34 | 19.333 | 21.619 |  | 6.4103 | 5267.34 | 5263 | 5271 | 5263 | 8 | 4.34 | 5271 | -4.34 | 3.66 | 3.66
" " | " " | DEVEX / ULTIMATE |  | 100 | 0.4724 |  | 783 | 345 | 42.8537 | 42.81 | 21.619 |  | 12.8145 | 5269.16 | 5263 | 5271 | 5263 | 8 | 6.16 | 5271 | -6.16 | 1.84 | 1.84
Tract 17 -Cabezon Subdivision | Existing | EXISTING |  | 100 | 0.4561 |  | 620 | 404 | 45.5576 | 44.3973 | 26.41 |  | 10.5393 | 5274.79 | 5263 | 5280 | 5263 | 17 | 11.79 | 5280 | -11.79 | 5.21 | 5.21
" " | " " | DEVEX / ULTIMATE |  | 100 | 0.4561 |  | 684 | 420 | 50.749 | 49.517 | 26.41 |  | 12.1417 | 5275.52 | 5263 | 5280 | 5263 | 17 | 12.52 | 5280 | -12.52 | 4.48 | 4.48
Stone Bridge Subdivision | Existing | EXISTING |  | 100 | 0.0878 |  | 150 | 29 | 7.7799 | 7.7509 | 4.2012 |  | 3.9985 | 5249.86 | 5246 | 5250 | 5246 | 4 | 3.86 | 5250 | -3.86 | 0.14 | 0.14
" " | " " | DEVEX / ULTIMATE |  | 100 | 0.0878 |  | 161 | 49 | 8.7817 | 8.7462 | 4.2012 |  | 4.2745 | 5250.04 | 5246 | 5250 | 5246 | 4 | 4.04 | 5250 | -4.04 | -0.04 | -0.04
19th Ave. Retention Pond (east of Golf Course Rd) [B] | " " | EXISTING |  | 100 | 0.5935 |  | 692 | 0 | 43.9782 | 0 | 15.8396 |  | 15.8396 | 5234 | 5218 | 5232 | 5218 | 15 | 16 | 5233 | -2 | -2 | -2
Black Arroyo Dam | Existing | EXISTING |  | 100 | 9.567 |  | 8539 | 3045 | 709.3905 | 708.181 | 537.33 |  | 286.682 | 5165.61 | 5146 | 5165.75 | 5146 | 29 | 19.61 | 5175 | -19.61 | 0.14 | 9.39
" " | " " | DEVEX |  | 100 | 9.567 |  | 9864 | 4649 | 867.4591 | 865.738 | 537.33 |  | 328.3439 | 5167.33 | 5146 | 5165.75 | 5146 | 29 | 21.33 | 5175 | -21.33 | -1.58 | 7.67
" " | " " | ULTIMATE |  | 100 | 9.567 |  | 6923 | 2956 | 865.8519 | 864.1184 | 537.33 |  | 265.8398 | 5164.73 | 5146 | 5165.75 | 5146 | 29 | 18.73 | 5175 | -18.73 | 1.02 | 10.27
" " | " " | ULTIMATE |  | 500 | 9.567 |  | 9498 | 5686 | 1156.2996 | 1154.4623 | 537.33 |  | 345.4586 | 5168.02 | 5146 | 5165.75 | 5146 | 29 | 22.02 | 5175 | -22.02 | -2.27 | 6.98
Proposed Detention Facilities
Sugar Pond | Proposed | ULTIMATE |  | 100 | 0.092 |  | 122 | 37 | 6.9582 | 6.8791 | 4.511 |  | 2.6549 | 5640.39 | 5638 | 5647 | 5633 | 14 | 7.39 | 5647 | -2.39 | 6.61 | 6.61
Sugar Pond | " " | ULTIMATE |  | 500 | 0.092 |  | 170 | 42 | 9.6154 | 9.531 | 4.511 |  | 4.1769 | 5642.03 | 5638 | 5647 | 5633 | 14 | 9.03 | 5647 | -4.03 | 4.97 | 4.97
Lisbon Pond | Proposed | ULTIMATE |  | 100 | 0.62 |  | 755 | 74 | 41.8619 | 41.1739 | 41.1267 |  | 27.7657 | 5598.96 | 5595 | 5601 | 5589 | 13 | 9.96 | 5602 | -3.96 | 2.04 | 3.04
Lisbon Pond | " " | ULTIMATE |  | 500 | 0.62 |  | 1089 | 222 | 58.7775 | 58.0762 | 41.1267 |  | 39.5777 | 5601.65 | 5595 | 5601 | 5589 | 13 | 12.65 | 5602 | -6.65 | -0.65 | 0.35
19th Ave. Dam | Proposed | ULTIMATE |  | 100 | 4.024 |  | 3408 | 1499 | 288.4143 | 286.5536 | 155.2656 |  | 92.5388 | 5293.53 | 5285 | 5297 | 5279 | 18 | 14.53 | 5297 | -8.53 | 3.47 | 3.47
19th Ave. Dam | " " | ULTIMATE |  | 500 | 4.024 |  | 4983 | 2421 | 401.4429 | 400.5521 | 155.2656 |  | 132.351 | 5297.69 | 5285 | 5297 | 5279 | 18 | 18.69 | 5297 | -12.69 | -0.69 | -0.69
a - See Appendix B - Watershed Map Tiles
b - EXISTING basin development conditions and existing infrastructure. DEVEX - Full basin development with existing infrastructure. ULITIMATE - Full basin development including proposed infrastructure.
c - See Appendix D,E and F for HEC-HMS output results
d - See Appendix I for pond routing elevation - area- capacity - discharge data and sources
e- Negative number indicates the flow depth exceeds referenced elevation - no freeboard available for cells highlighted in red
[A] Relative Elevations Are Used
[B] Pond routing was not completed for 19th Ave. retention pond - It is clear that the 100-year runoff volume will far exceed the storage volume.This correlates well with a resident that lives near the pond that told Smith Engineers he has seen the pond full several times and it has flooded residents on the south side of the pond. The peak water surface elevation is just an estimate since the pond will spill in the 100-year 24-hour flood. Since the basin is fully developed, DEVEX and ULTIMATE results are not presented since no more development is possible and improvements are not proposed. The pond is owned and operated by the City of Rio Rancho.
Area verification - Sum of all Black Dam sub-basins external to HEC-HMS = 9.673 sq mi, HEC-HMS inflow drainage area = 9.673 sq mi
Don’t Use
Lisbon Pond | Proposed | Ultimate |  |  | 0.62 |  | 755 | 93 | 41.8619 | 41.3531 | 46.544 |  | 26.9942 | 5596.64 | 5595 | 5600 | 5589 |  | 7.64 | 5600 | -1.64 |  | 3.36
Lisbon Pond 1V:6H | Proposed | Ultimate |  |  | 0.62 |  | 755 | 270 | 41.8619 | 41.5379 | 27.841 |  | 22.4841 | 5600.26 | 5595 | 5600 | 5589 |  | 11.26 | 5602 | -5.26 |  | 1.74
Lisbon Pond 1V:4H | Proposed | Ultimate |  |  | 0.62 |  | 755 | 114 | 41.8619 | 41.5254 | 31.876 |  | 25.9352 | 5600 | 5595 | 5600 | 5589 |  | 11 | 5602 | -5 |  | 2
Lisbon Pond 1V:6H | Proposed Based On Pats Table | Ultimate |  |  | 0.62 |  | 755 | 95 | 41.8619 | 41.2075 | 55.683 |  | 26.9499 | 5596.96 | 5595 | 5602 | 5589 |  | 7.96 | 5602 | -1.96 |  | 5.04

## Routing Summary with Unser Box
TABLE
Detention Pond Routing Summary (Existing Conditions, DEVEX Conditions and Ultimate Conditions)
Addendum 1 - Black Arrroyo Watershed Management Plan
Detention Pond Name | Existing or Proposed Pond (detention or retention) | Development / Model Condition | Model Analysis Point Name | Return Period | Drainage Area | Storm Return Period (100-yr. 24-hr. duration) | Peak Inflow | Peak Outflow | Inflow Runoff Volume | Outflow Runoff Volume | Maximum Storage Volume (top of embank ment) | Peak Storage Volume | Peak Storage Volume | Peak Water Surface Elevation | Top of Principal Spillway Elevation | Emergency Spillway Elevation | Pond Invert Elevation | Max Pond Depth | Water Depth | Top of Pond Embank ment Elevation | Free board to Principal Spillway Elevation | Free board to Emergency Spillway Elevation | Free board to top of Pond Embank ment
[5 empty] | (sq mi) |  | (cfs) | (cfs) | (ac-ft) | (ac-ft) | (ac-ft) | (ft^3) | (ac-ft) | (ft) | (ft) | (ft) | (ft) | (ft) | (ft) | (ft) | (ft) | (ft) | (ft)
a | a | b | a |  |  |  | c | c | c | c | d | c | c | c | d | d | d | d |  | d | e |  | e
Wallen Sub division | Existing | Existing |  | 100 yr-24hr | 0.0154 |  | 19 | 1 | 0.569 | 0.568 | 5.8267 |  | 0.4589 | 5657.12 | 5655.88 | 5660 | 5655.88 | 9.12 | 1.24 | 5665 | -1.24 | 2.88 | 7.88
" " | " " | DEVEX |  | 100 yr-24hr | 0.0154 |  | 32 | 2 | 1.36 | 1.3534 | 5.8267 |  | 0.9634 | 5658.41 | 5655.88 | 5660 | 5655.88 | 9.12 | 2.53 | 5665 | -2.53 | 1.59 | 6.59
Sunset | " " | Existing |  | 100 yr-24hr | 0.2558 |  | 297 | 35 | 15.1475 | 15.147 | 25.5 |  | 9.2063 | 5617.06 | 5616.73 | 5620 | 5606 | 16 | 11.06 | 5622 | -0.33 | 2.94 | 4.94
" " | " " | DEVEX |  | 100 yr-24hr | 0.2558 |  | 349 | 37 | 20.3148 | 20.3244 | 25.5 |  | 11.8589 | 5618.35 | 5616.73 | 5620 | 5606 | 16 | 12.35 | 5622 | -1.62 | 1.65 | 3.65
Sugar Ridge Sub division | " " | Existing |  | 100 yr-24hr | 0.62 |  | 242 | 235 | 10.222 | 9.721 | 2.6759 |  | 1.593 | 5568.38 | 5561.13 | 5567.26 | 5560 | 11 | 8.38 | 5571 | -7.25 | -1.12 | 2.62
Sugar Ridge Sub division | " " | Existing -1 |  | 100 yr-24hr | 0.62 |  | 105 | 94 | 5.148 | 4.648 | 2.6759 |  | 1.234 | 5567.36 | 5561.13 | 5567.26 | 5560 | 11 | 7.36 | 5571 | -6.23 | -0.1 | 3.64
" " | " " | DEVEX |  | 100 yr-24hr | 0.62 |  | 299 | 289 | 14.795 | 14.287 | 2.6759 |  | 1.6968 | 5568.66 | 5561.13 | 5567.26 | 5560 | 11 | 8.66 | 5571 | -7.53 | -1.4 | 2.34
Lisbon Pond 1V:6H | Proposed Based On Pats Table | Ultimate |  |  | 0.62 |  | 755 | 111 | 41.8619 | 41.3844 | 32.8322 |  | 25.4583 | 5600 | 5595 | 5602 | 5589 | 13 | 11 | 5602 | -5 |  | 2
Lisbon Pond 1V:6H | Proposed Based On Areas from CAD 4-23-13 | Ultimate |  |  | 0.62 |  | 755 | 110 | 41.8619 | 41.3994 | 33.5279 |  | 25.5222 | 5599.88 | 5595 | 5601 | 5589 | 13 | 10.88 | 5602 | -4.88 |  | 2.12
Lisbon Pond 1V:6H | Proposed Based On Areas from CAD 4-23-13 | Ultimate |  | 100 yr-24hr | 0.62 |  | 755 | 110 | 41.8619 | 41.3994 | 33.5279 |  | 25.5222 | 5599.88 | 5595 | 5601 | 5589 | 13 | 10.88 | 5602 | -4.88 | 1.12 | 2.12
Lisbon Pond 1V:6H | Proposed Based On Areas from CAD 4-23-13 | Ultimate |  | 500 yr-24hr | 0.62 |  | 1089 | 513 | 58.7775 | 58.306 | 33.5279 |  | 32.9828 | 5601.88 | 5595 | 5601 | 5589 | 13 | 12.88 | 5602 | -6.88 | -0.88 | 0.12
Sugar Pond | Proposed | Ultimate |  | 100 yr-24hr | 0.092 |  | 122 | 28 | 6.9582 | 6.9398 | 4.511 |  | 2.7838 | 5644.31 | 5638 | 5647 | 5633 | 14 | 11.31 | 5647 | -6.31 | 2.69 | 2.69
19th Ave Pond- Including Undetained Flows from Tributary 'A' arroyo.Up - stream facilites include Lisbon and Sugar Ponds | Proposed | Ultimate |  |  | 4.024 |  | 3413 | 970 | 288.607 | 286.712 | 129.6453 |  | 115.7311 | 5295.61 | 5285 | 5296 | 5279 | 18 | 16.61 | 5297 | -10.61 | 0.39 | 1.39
Footnotes for Detention Pond Routing Summary Table
a - See Drainage Basin Maps
b - Existing - Existing development conditions and existing infrastructure. DEVEX - Developed - Full basin development with existing infrastructure. Ultimate - Full basin development including proposed infrastructure.
c - See HEC-HMS output for results
d - See Appendix ?? for pond routing elev-area-capacity-discharge data and sources
e- Negative number indicates the flow depth exceeds referenced elevation - no freeboard available
A Pond Routing was not completed for this retention pond - It is clear that the 100-year runoff volume will far exceed the storage volume.
This correlates well with a resident that lives near the pond that told Smith Engineers he has seen the pond full and it has flooded residents on the south side of the pond.
The Peak Water Surface Elevation is just a guess since the pond will spill in the 100-year 24-hour flood.
Note - Basin Fully Developed, therefore DEVEX Tc and DEVEX Tp results are the same as existing
blue - may get better data from as-builts (CORR said these are not yet available)
Area verification - Sum of all Black Dam sub-basins external to HEC-HMS = 9.673 sq mi, HEC-HMS inflow drainage area = 9.6717 sq mi
Summary of Peak Discharges Realtive to the Unser Box Culvert Crossing
Location | As-Built Capacity | Computed Capacity |  |  | Existing Conditions Dishcarge at Culverts |  | Devex Discharge at Culverts | Ultimate Conditons Discharge at Culverts | Included Ultimate Facilties
| cfs | cfs |  |  | cfs |  | cfs | cfs
| a | b |  |  | c |  | c | c
Unser Blvd & Westside Blvd | 2680 | 3100 |  |  | 3844 |  | 4513 | 1492 | Sugar Pond
Lisbon Pond
19th Avenue Dam
Footnotes Summary of Peak Discharges Realtive to the Unser Box Culvert Crossing
a- Sheet D1 by Hiutt-Zollars dated August 5,2008
b- Results from Culvert Master
c- Results from HEC-HMS Models
Values in Red Indicate lack of capacity
Wexford Pond | " " | Existing |  |  | 0.2326 |  | 368 | 135 | 27.897 | 27.879 | 12.5 |  | 9.2655 | 40.04 | 31.5 | 40 | 31.5 | 10 | 8.54 | 41.5 | -8.54 | -0.04 | 1.46
" " | " " | DEVEX |  |  | 0.2326 |  | 368 | 135 | 27.6672 | 27.6653 | 12.5 |  | 9.2614 | 40.03 | 31.5 | 40 | 31.5 | 10 | 8.53 | 41.5 | -8.53 | -0.03 | 1.47
Gateway | " " | Existing |  |  | 0.4724 |  | 503 | 265 | 19.34 | 19.333 | 21.619 |  | 6.4103 | 5267.34 | 5263 | 5271 | 5263 | 8 | 4.34 | 5271 | -4.34 | 3.66 | 3.66
" " | " " | DEVEX |  |  | 0.4724 |  | 783 | 345 | 42.8537 | 42.81 | 21.619 |  | 12.8145 | 5269.16 | 5263 | 5271 | 5263 | 8 | 6.16 | 5271 | -6.16 | 1.84 | 1.84
Tract 17 -Cabezon Subdivision | Existing | Existing |  |  | 0.4561 |  | 620 | 404 | 45.558 | 44.3973 | 26.41 |  | 10.5393 | 5274.79 | 5263 | 5280 | 5263 | 17 | 11.79 | 5280 | -11.79 | 5.21 | 5.21
" " | " " | DEVEX |  |  | 0.4561 |  | 684 | 420 | 50.749 | 49.517 | 26.41 |  | 12.1417 | 5275.52 | 5263 | 5280 | 5263 | 17 | 12.52 | 5280 | -12.52 | 4.48 | 4.48
Stone Bridge Sub division | Existing | Existing |  |  | 0.0878 |  | 150 | 29 | 7.7782 | 7.75 | 4.2012 |  | 3.9985 | 5249.86 | 5246 | 5250 | 5246 | 4 | 3.86 | 5250 | -3.86 | 0.14 | 0.14
" " | " " | DEVEX |  |  | 0.0878 |  | 161 | 49 | 8.7817 | 8.7462 | 4.2012 |  | 4.2745 | 5250.04 | 5246 | 5250 | 5246 | 4 | 4.04 | 5250 | -4.04 | -0.04 | -0.04
Black Arroyo Dam | Existing | Existing |  |  | 9.6717 |  | 8638 | 3091 | 719.2537 | 718.0244 | 537.33 |  | 291.6151 | 5165.82 | 5146 | 5165.75 | 5146 | 29 | 19.82 | 5175 | -19.82 | -0.07 | 9.18
" " | " " | DEVEX |  |  | 9.6717 |  | 9989 | 4803 | 878.4814 | 876.7318 | 537.33 |  | 330.9047 | 5167.44 | 5146 | 5165.75 | 5146 | 29 | 21.44 | 5175 | -21.44 | -1.69 | 7.56
19th Ave. Retention Pond (east of Golf Course Rd) | " " | Existing |  |  | 0.5935 |  | 692 | 0 | 43.9782 | 0 | 15.8396 |  | 15.8396 | 5234 | 5218 | 5232 | 5218 |  | 16 | 5233 | -2 |  | -1
Don’t Use
Lisbon Pond | Proposed | Ultimate |  |  | 0.62 |  | 755 | 93 | 41.8619 | 41.3531 | 46.544 |  | 26.9942 | 5596.64 | 5595 | 5600 | 5589 |  | 7.64 | 5600 | -1.64 |  | 3.36
Lisbon Pond 1V:6H | Proposed | Ultimate |  |  | 0.62 |  | 755 | 270 | 41.8619 | 41.5379 | 27.841 |  | 22.4841 | 5600.26 | 5595 | 5600 | 5589 |  | 11.26 | 5602 | -5.26 |  | 1.74
Lisbon Pond 1V:4H | Proposed | Ultimate |  |  | 0.62 |  | 755 | 114 | 41.8619 | 41.5254 | 31.876 |  | 25.9352 | 5600 | 5595 | 5600 | 5589 |  | 11 | 5602 | -5 |  | 2
Lisbon Pond 1V:6H | Proposed Based On Pats Table | Ultimate |  |  | 0.62 |  | 755 | 95 | 41.8619 | 41.2075 | 55.683 |  | 26.9499 | 5596.96 | 5595 | 5602 | 5589 |  | 7.96 | 5602 | -1.96 |  | 5.04