January 31, 2012

Genevieve L. Donart, P.E.

Isaacson & Arfman, P.A.

128 Monroe St. NE

Albuquerque, NM 87108

Re:	Lot 2, McMahon Marketplace

Conceptual Grading and Drainage Plan

Engineer’s Stamp Date (none),  A11/D011A

Dear Ms. Donart,

Based upon the information provided in your submittal received 1/12/2012, the above referenced report is approved for Site Plan for Subdivision.  The following comments have to be addressed prior to an approval for Grading and Building Permits:

- This grading plan does not exactly follow the overall basin layout.  Provide proposed basin layout based on the Lot 2 grading plan.  Provide capacity calculations for the inlets which may be impacted by these changes.

- Include a City of Albuquerque BM on the plan (NAVD 88).

- Add Legends.

- Show roof flow directions.

- It appears that the spot elevation “7.50” by the ramps should be “8.50”.

- How will the offsite runoff from the south drain through this site?  Will there be a desilting pond?

- Provide additional top and bottom of wall elevations for the proposed retaining wall.  Please call out the stem wall and size located on the south side of the building.

- If a restaurant is being proposed the trash enclosure area(s) must drain to the sewer system, and detail grades have to be added to the plan.

- Please make sure that the existing storm drain system is draining properly.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

C:	File