May 15, 2012

James D. Hughes, P.E.

Mark Goodwin & Associates, PA

P.O. Box 90606

Albuquerque, NM 87199

Re:  The Team Office Building Grading and Drainage Plan

Conceptual (C-12/D026)

Dear Mr. Hughes,

Based upon the information provided in your submittal dated 05-03-12, the above referenced plan cannot be approved conceptually until the following comment is addressed:

- It appears the outfall on the southern edge of the property will require approval from

the State Highway Department before it can be utilized in the drainage plan.

Prior to Building Permit approval the following comments need to be addressed:

- The right-of-way on the western edge of the property is county owned and any

required roadway improvements will need to be addressed prior to construction.

- The outflow from Basin 102 of 22.8 cfs does not match the figure in the North Coors

DMP of 8 cfs for Basin 13.1W, please clarify this value.

- How does the proposed detention pond adequately mitigate both accepting the offsite

flows from Basins 103 and 104 as well as any increases in onsite runoff? Please

provide pond calculations.

- How will the outfall on the southern edge of the property be protected from offsite

flows?

- Please provide sidewalk culvert details for the central sidewalk portion of the project.

Will it be covered?

- All benchmarks and elevations should be referenced to NAVD 88 standards.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

# C:file

CJH