June 25, 2013

Ronald R. Bohannan, P.E.

Tierra West, LLC

5571 Midway Park Pl NE

Albuquerque, NM 87109

Re:	Albuquerque Sporting Center, Tract A-1, Albuquerque West Unit 2

Grading and Drainage Plan,

Engineer’s Stamp dated 6-05-13 (C13/D029)

Dear Mr. Bohannan

Based upon the information provided in your submittal received 6-6-13, the above referenced grading and drainage plan is approved for Phase-I Site Plan for Building Permit and Phase-I Building Permit only.  The following comments have to be addressed prior to approval of Phase-II:

- The proposed 30’ curb opening along Paradise Boulevard may be a safety issue.  If so, an alternative design would be required to intercept the runoff. Provide calculations for the 30’ opening.

- Section B-B drainage calculation is shown to have a 1.44’ water depth, but the section shown on the plan only calls out for a one foot high curb.  The cul-de-sac and the entrance to the concrete channel should be modified to intercept all the runoff.

- It is not clear how the cobble swale or the lid pond drain out into the cul-de-sac.  A 40’ curb opening calculations was provided.  Show the location of the 40’ curb opening on the plan.

An Erosion Sediment Control Plan is required.  This project requires a National Pollutant Discharge Elimination System (NPDES) permit for storm water discharge for disturbing one acre or more and a Topsoil Disturbance Permit for disturbing ¾ of an acre or more.  Please attach a copy of this approved plan to the construction sets prior to sign-off by Hydrology.

Prior to Certificate of Occupancy release the following items are required:

- Engineer Certification per the DPM checklist.

- An acceptance letter from NMDOT on the construction of the 10’ Asphalt Trail and the Swale along Paseo Del Norte.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development Review Services

C:	e-mail