November 13, 2013

Richard J. Berry, Mayor

Ms. Genny Donart, P.E.

Isaacson & Arfman, P.A.

128 Monroe St. NE

Albuquerque, New Mexico  87108

RE:	Applebee’s at Holly Place   						B13-D022A

North Alb. Acres, Tract A, Unit B, Block 18, Lot 20 & Holly Place, Tract B

Conceptual Grading & Drainage Plan for Site Development Plan

PE Stamp:  10/23/2013

Dear Ms. Donart:

Based upon the information provided in your submittal received 10-23-2013 and supporting documentation received 10/28/13, the above referenced is approved for Site Development Plan for DRB action.

A separate submittal will be required for Building Permit.  Per your discussion your discussions with Curtis Cherne and comments on my 9/23/13 letter, there are a few issues to be resolved on this plan for us to approve it for Building Permit.  See the back of this letter for a brief summary of those points.

If you have questions, please email me at grolson@cabq.gov or phone 505-924-3994.

Sincerely,

Gregory R. Olson, P.E.

Senior Engineer

Orig:	Drainage file   C18/D073A

c.pdf	Addressee via Email  GennyD@IAcivil.com

Please review and address the following issues for Building Permit approval:

- Ponding along the western edge of the site proposes rundown pipes that will be exposed above grade, west of the curb.  Reference Detail 5 on Sheet CG-501.  Stabilize this design for Building permit.

- Clarify developed site flow conditions: On the Basin Map, label the new basin discharge points and rates at detention pond inlets and outlets, and where flows enter and leave the site.

- Please advise your client that because this site exceeds 1.0 acre, any Grading or Building on this site will require a Storm Water Pollution Prevention Plan (SWPPP).  Also, an Erosion and Sediment Control (ESC) Plan, prepared by a NM Registered Professional Engineer, must be submitted to and approved by this office, prior to Building Permit approval and start of grading.