November 30, 2011

Mike J. Walla, P.E.

Walla Engineering, LTD

6100 Indian School NE, Suite 105

Albuquerque, NM 87110

Re:	MCT Industries Paint Booth Replacement, Grading and Drainage Plan, 	Engineer’s Stamp Dated 11-07-2011 (D17/D047)

Dear Mr. Walla,

Based upon the information provided in your submittal dated 11-08-2011, the above referenced plan can not be approved for Building Permit until the following comments are addressed:

- Include all the offsite runoffs and explain how it will impact this site.

- Provide proposed pond calculations.  Show the 100-Yr WSEL.  Provide emergency overflow and calculations.

- Are there any slope protection being proposed for the pond at the end of the valley gutter and the 8” pipe.

- The top of pond elevation is “FG 79.90” next to a proposed contour with an elevation of 76.00.  Please correct this elevation.

- There is existing hatch area to the east of the retention pond.  Please note on the plan what this area is and were to and how does it drain.

- Another hatch area is shown on the east side of the building.  Please indicate what this hatch area is.

- There is an area just west of the new building where the runoff ponds against the existing wall.  Will this area be regarded?

- Does the pond to the north have adequate volume for the existing developed runoff for the northerly portion of this site?

- If  ¾ acre or more is being disturbed Topsoil Disturbance Permit will be required.

- If one acre or more is being disturbed this project requires a National Pollutant Discharge Elimination System (NPDES) permit for storm water discharge.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, PE

Senior Engineer, Planning Dept.

Development and Building Services

# C:	file