August 12, 2014

Mr. Fred C. Arfman, PE

Isaacson & Arfman, PA

1287 Monroe Street NE

Albuquerque, NM 87108

Re:	Resort Lifestyle Communities

Conceptual Grading and Drainage Plan

No Engineer’s Date (D18D054C)

Dear Mr. Arfman,

Based upon the information provided in your submittal received 7-14-14, the above referenced plan is approved for Site Development Plan action by EPC.  Address the following comments with the DRB submittal.

- Previously, you had received Hydrology comments for EPC regarding this site.  The comments were to manage the first flush and provide calculations on a revised Conceptual Grading and Drainage Plan.  The purpose of this comment was to make sure you had sufficient room with the proposed layout for the water harvesting.  No water harvesting ponds or calculations were provided with the resubmittal.  Please provide them with the next submittal.

Per the City Drainage ordinance, the 90th Percentile Storm Event, which is 44 inches, is to be managed. Reduce 0.44 inch by the 0.1 inch for the initial impervious abstraction in Table A-6 of Section 22 of the DPM.  Multiply the remaining 0.34 inch by your impervious area.  This is the portion to retain.

- Isaacson and Arfman prepared the Santa Monica Tracts 1-4 Master Drainage Report which was approved and which includes the area of this site.  The MDP included provisions for the development of Tracts 3 and 4.  However, the MDP did not address further subdivision of Tracts 3 and 4 which was not expected at that time.  Update the MDP to reflect the proposed subdivision of Tracts 3 and 4.  Discuss which property or properties that will be responsible for installing the proposed 42 inch and 36 inch storm drain across Tract 3 and removing the existing pond and storm pipe on Tract 3.  Also address the interim conditions as each smaller tract develops without the others developing.

Although Tracts 1 through 4 have a cross-lot drainage easement from the Bulk Land Plat, provide a low erosive interim solution such as rip-rap for drainage from the proposed Tract 4A to the existing standpipe in the current Tract 3.

San Vicente Avenue was not included in the basins for this site.  Include San Vicente Avenue in the basin and flow analysis when updating the MDP.

If you have any questions, you can contact me at 924-3994.

Sincerely,

Amy L. D. Niese, P.E.

Senior Engineer, Hydrology

Planning Department

C:	e-mail

file