June 4, 2012

Christian J. Sholtis, P.E.

Bohannan Huston, Inc.

7500 Jefferson NE

Albuquerque, NM 87109

Re:	US New Mexico Federal Credit Union

Tract 5, Andalucia at La Luz

Conceptual Grading and Drainage Plan

Engineer’s Stamp Date 5/18/2012 (E12/D015D1)

Dear Mr. Sholtis,

Based upon the information provided in your submittal received 4/18/2012, the above referenced submittal is approved for Building Permit and Grading Permit.

The following comments are to be addressed prior to Certification of Occupancy:

- Pond A has to be modified and as-built grades and volume calculations should be provided.

- If Pond A will not be modified the proposed temporary retention pond has to be in place along with the recorded drainage easement.

- As previously mentioned grout is not a preferred method for plugging the pipe, because there is the possibility of debris in the downstream public storm drain.

If you have any questions, you can contact me at 924-3965

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

C:	e-mail