March 19, 2012

Jean J. Bordenave, P.E.

Bordenave Designs

P.O. Box 91194

Albuquerque, NM 87199

Re:	Rice/McGonagil Residence Grading and Drainage Plan

Engineer’s Stamp Date 02/20/2012 (E14/D007)

Dear Mr. Bordenave,

Based upon the information provided in your submittal received 02/28/2012, the above referenced Grading and Drainage Plan can not be approved for Building Permit until the following comments have to be addressed:

- Street names on the Vicinity Map are not clear.  Please mark the location of the site on the Vicinity Map.

- Call out wall openings for the proposed wall on the west side of the building.

- Basin B top of pond is 82.3 under the volume calculations and on the plan view is 82.20.

- Provide proposed grades in front of the garage (+/- 82.75’).  Top of concrete just east of the garage is at 82.90. Therefore, the runoff appear to be draining towards the garage.

- Note 3 should be used instead of Note 6 for the proposed driveway.

- Total area under the proposed conditions is more that existing conditions.

- Provide 10 year/6 hour volume calculations under proposed conditions.  Volume increase appears to be more than what is called under the “GRADING NOTES”.

- Need to lower top of Basin B Pond to allow the runoff from the street enter the pond.  Bottom of the pond had two different elevations (80.70 & 81.00).

- Clearly show the limits of Basin A and B.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

C:	e-mail