August 29, 2012

Gilbert Aldaz, P.E.				galdaz47@yahoo.com

Applied Engineering & Survey

1605 Blair Dr. NE

Albuquerque, NM  87112

Re:	Gardner Zemke Addition, 6821 Academy Parkway West NE,

Request for Permanent C.O.  – Not Accepted

Engineer’s Stamp dated: 01-04-12, (E17/D001)

Certification dated: 08-22-12

Dear Mr. Aldaz,

Based upon the information provided in the Certification received 08-24-12, the above referenced Certification is unacceptable for release of a Permanent Certificate of Occupancy by Hydrology.

- It appears a six inch curb was constructed on the western property line in lieu of an eight inch curb.  Please provide calculations demonstrating a six inch curb prevents flows from leaving the site.

- Please certify the pond volume.

- The Engineer’s certifying language will need to be per the DPM, see enclosed.

If you have any questions, you can contact me at 924-3986.

Sincerely,

Curtis A. Cherne, P.E.

Principal Engineer—Hydrology, Planning Dept.

Development and Building Services

C:	File

Enclosure (1)