March 15, 2013

David Soule, P.E.

Rio Grande Engineering

P.O. Box 93924

Albuquerque, NM 87199

Re:	900 Griegos Road Townhomes Grading and Drainage Plan

Engineer’s Stamp date 03-06-13 (F-14/D067)

Dear Mr. Soule,

Based upon the information provided in your submittal received 03-06-13, the above referenced Grading and Drainage Plan is approved for Building Permit with the following comments:

- Please make sure that the as-built elevations clearly will show the bottom elevation (4972.00) for the proposed pond at the southeast corner of the property; this contour is still absent in the revised plan set.

This project requires a National Pollutant Discharge Elimination System (NPDES) permit for storm water discharge for disturbing one acre or more and a Topsoil Disturbance Permit for disturbing ¾ of an acre or more.

Please attach a copy of this approved plan to the construction sets prior to sign-off by Hydrology.  Prior to Certificate of Occupancy release, Engineer Certification per the DPM checklist will be required.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

C:	e-mail