11

X

July 7, 2008

David Thompson, P.E.

Thompson Engineering

P.O. Box  65760

Albuquerque, New Mexico  87193

RE:	VIA SENDEROS SUBDIVISION – College Park West, Tract F  (G10 – D 007 A)

Drainage Plan for Building Permit  	(PE Stamped 05-29-08)

Dear Mr. Thompson:

Based upon the information provided in your submittal received on 6-05-2008, the above referenced plan cannot be approved for Preliminary Plat or Grading Permit until the following comments are addressed:

- The Drainage Report indicates no offsite flows reach the site, however contours on the grading plan show at least some of Tract E draining into Tract F from the west.  Quantify these flows and address handling them with development of Tract F.

- The Master Drainage Plan prepared by Espey-Huston & Assoc. for College Park West also proposed surface discharge of Tract F to St. Josephs Ave., but at a developed rate of 6.03 cfs, Q100-6 Hr.  Your proposed rate of 8.82 cfs must be reduced to the 6.03 cfs rate,    -OR- you must provide analysis to show that surface flow capacity exists downstream through the rundown on 67th Street, to convey this increased rate.

- Clarify the intent for the “Undeveloped” Parcel, Lot A.  Will it be graded?  Provide stabilization to keep sediment from entering the public R/W on Tallado Court.

- Provide a typical street cross section for Tallado Court and/or contours on Lot A to clearly show and ensure the erosion control requested in item 3, above.

- In the typical Lot Grading Plan, where is dimension “D1” and should the last note end with a reference to “SPOT   6 “ ?

- Since the site is 2.7 acres, remember that a SWPPP will be required.

If you have any questions or would like to schedule a meeting to discuss this, you may contact me at 924-3981.

Sincerely,

Gregory R. Olson, P.E.

Hydrology Section

XC:	Bradley Bingham, COA-PLN/Hydrology

file G10 – D 007 A