July 26, 2012

Levi Valdez, P.E.

George T. Rodriguez Development & Consulting

12800 San Juan NE

Albuquerque, NM 87123

Re:	San Clemente Apartments, Lots 5 & 6  Grading and Drainage Plan

Engineer’s Stamp date 07-03-2012 (G-14/D006A)

Dear Mr. Valdez,

Based upon the information provided in your submittal received 07-06-2012, the above referenced plan cannot be approved for Building Permit until the following comments are addressed:

- The existing site topography appears to mostly consist of Treatment Type A which does not concur with the Type C used to calculate the existing discharge from the site.

- Please provide volume calculations for the proposed water harvesting areas.

- All discharge from the site will be limited to 2.75 cfs/acre.

- Provide additional flow line and top-of-curb elevations at each of the two proposed curb cuts.

- Easements will be necessary for the two shared dumpster enclosures.

- Include details for the swales located on the western and eastern edges of the property.

- Please use NAVD 88 for the benchmark designation.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

C:	Email