August 12, 2011

David Soule, P.E.

Rio Grande Engineering

P.O. Box 67305

Albuquerque, NM 87193

Re:	HUESTAS DE LA FE Church Expansion

Grading and Drainage Plan

Engineer’s Stamp date 8-10-11 (G-15/D104)

Dear Mr. Soule,

Based upon the information provided in your submittal received 8/10/11, the above referenced plan cannot be approve for Building Permit or Grading Permit until the following comments are addressed:

- A basin map is needed for the new building configuration, also showing the AH flood zone at the west end of this site.

- Is there an addition or are you just adding the inlets?

- An SO-19 is required to tie into the existing inlet. Add SO-19 notes to plan.

- It is difficult to confirm your land treatment calculations for this site please adjust your plan accordingly.

- Give elevation points from the surrounding sites.

- Prior to CO, an Elevation Certificate for the existing structure in the AE Flood Zone is required.

- A Floodplain Development Permit is required for the proposed building in the AE Flood Zone.

- Flows must be maintained at or below historic values.

- Provide inlet calculations with a 50% clogging factor.

- Provide the 100 year WSEL.

- Why was this site not built per approved plan dated 6/4/09?

Hydrology is requesting that proposed landscape areas be depressed to retain/infiltrate the rain that falls on them.

If you have any questions, you can contact me at 924-3695, or Rudy Rael at 924-3977.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

RER/SB

C:	File