December 12, 2013

Mike Walla, P.E.

Walla Engineering

6501 Americas Parkway, Suite 301

Albuquerque, NM 87110

Re:	Comanche Elementary School Phase I

Grading and Drainage Plan

Engineer’s Stamp Date 11/18/2013 (G19/D037)

Dear Mr. Walla,

Based upon the information provided in your submittal received 11-19-13, the grading and Drainage Plan provided cannot be accepted for grading permit and building permit until the following comments are addressed.

- Calculations are required for existing flows and new flows. What is the allowable discharge from this site?

- Inverts are missing, along with slopes.

- Where does the paved channel lead to?

- What do the darkened and slated circles represent?

- In which direction and where do the roof flows head?

- The area to the east of the new building, is this a new parking lot or is it existing buildings? Where do these flows head?

- Is the entry/exit lane new or existing? If new, where are the water blocks?

- A detail of the retaining wall near the head wall is needed.

- It appears that there is not adequate depth at the header wall. The pipe appears to daylight before the header wall. This area needs to be adjusted.

If you have any questions, you can contact me at 924-3695 or Rudy Rael at 924-3977.

Sincerely,

Shahab Biazar, P.E.

Principal Engineer, Planning Dept.

Development Review Services

RR/SB

C:	e-mail