November , 2014

David Soule, P.E.

Rio Grande Engineering

PO Box 93924

Albuquerque, New Mexico  87199

RE:	Noon Day, 2500 2nd St

Grading and Drainage Plan

Engineers Stamp Date 12/05/13 (H14-D067)

Engineer’s Certification Date 11/4/2014

Dear Mr. Soule,

Based on the Certification received 11/12/2014, the site is acceptable for a TEMPORARY 30- day Certificate of Occupancy by Hydrology.

Prior to permanent C.O., the following conditions must be met or repaired:

- provide calculations showing that the as-built width of the  north sidewalk culverts is sufficient for drainage.  It is built 17” wide but G&D calls for a 24” wide.

- On the north culvert, there is no expansion on both ends.  Give room to have the 6” space for expansion on both ends. There is also no bar on street end of plate.

- The south culvert has a cracked center with missing concrete at face creating a tripping hazard.  Recommendation is to remove south culvert, saw cut at cold joint ramp end.

- There is a cracked north side curb at cold joint through the back of curb, epoxy over bolts

If you have any questions, you can contact me at 924-3695.

Sincerely,

Rita Harmon, P.E.

Senior Engineer, Planning Dept.

Development Review Services

Orig:	Drainage file

c.pdf:	via Email:  recipient, CO Clerks—Katrina Sigala, Francis Connor, Carol Quintana