January 20, 2012

Jeff Mulbery, P.E.

Bohannan Huston, Inc.

7500 Jefferson NE

Albuquerque, NM 87109

Re:	APS Community Sports Stadium, Conceptual Grading and Drainage Plan, (J08/D002) Parcel C-1, Westland North

Dear Mr. Mulbery,

- Based upon the information provided in your submittal received December 21, 2011, the above referenced plan is approved for Grading only (no grading is allowed within the floodplain at this time).  The following comments have to be addressed prior to approval of Building Permit:

- Need to see the proposed storm drain system for Basin OS1 and Basin 18 as well as the proposed grades and storm drain system on Arroyo Vista Boulevard.

- There are additional offsite runoff south and west of the Basin OS4 which enter this site.

- Double check the flow quantities for the proposed storm drain pipes.

- Easement will be required for SD43 for the portion that is outside the APS property.  Will PNM approval be required to work within their easement?  Please make sure that the proposed location of the MH and the storm drain pipe will not have an impact on the existing power poles.

- Curb opening are needed where the inlets are located within the landscaping areas.

- Inlets 27 through 29 and the discharge pipe from Inlet 29 (18” SD pipe) are not shown on the tables.

- Provide detail for the quality manhole passed MH12.

- Provide details for the concrete rundowns.

- Only Basin OS3 is shown to drain to Inlet 9.1, and there is a pipe that extends west from Inlet 9.1 and captures portion of Basin OS4.

January 20, 2012

Page 2

- A CLOMAR submittal is required.

- AMAFCA’s approval is required.

- Arroyo Vista Boulevard drainage analysis and Construction Plans submittal to DRC are required.

- This project requires a Topsoil Disturbance Permit and a National Pollutant Discharge Elimination System (NPDES) permit for storm water discharge.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

# C:	File