October 20, 2011

Jeff Mulbery, P.E.

Bohannan Huston, Inc.

7500 Jefferson NE

Albuquerque, NM 87109

Re:	APS Community Sports Stadium, Conceptual Grading and Drainage Plan, (J08/D002) Parcel C-1, Westland North

Dear Mr. Mulbery,

Based upon the information provided in your submittal received October 4, 2011, the above referenced plan we have the following comments:

- Include a Vicinity Map and FIRM Map.

- BM for the project appears to have the wrong Northing and Easting Information.

- Show the floodplain limits on the Plan.

- Sheet DMP-001 appears to have a scale of 1”=100’.

- Show all the Offsite Basins and how they will drain through this site.

- Under the Proposed conditions it is mentioned that there are 19 On-Site Basins and 28 Basins are shown.

- How was the size of the ripraps determined?  Provide calculations.

- All the on-site basin have a treatment of D=90% and A=10%, and the offsite basins have a treatment C=100%.  Are these correct?

- Include the grate and invert elevations for all the drop inlets.  Also include all the pipes sizes and amount runoff being intercepted by each pipe.

- Provide additional spot elevations around the inlets to assure that inlets do intercept the amount runoff they are intended to intercept.

- Where does basin 19 drains to?

- Please label SD 22A and 22B on the plan.

- SD 44 only take the runoff from SD 27.  Please modify the table and the pipe size for SD 44.

- SD 43 is not labeled on the plan.

- SD 45 takes the runoff from SD 43 and SD 44.  Please correct the table.

- Where does SD 45 drain to?

October 20, 2011

Page 2

- Is portion of Basin 26 draining to Basins 21 & 23? If so, please modify the basin boundaries.

- What is the size of the outflow pipe from the detention pond shown within basin 17.  Add the pipe size to the Table.

- What are the proposed slope protections?

- Provide street flow calculations as well as the inlet capacity calculations.  Are inlets 26, 27, and 28 intercepting the same amount of runoff?

- Relocate the proposed inlet shown in the driving lane on the westerly entrance.

- Provide the inlet types and pipe sizes proposed within Basin OS1.

- Provide drainage calculations for Arroyo Vista Boulevard.

- Provide a copy of the plat for this project.

- A Separate Basin Layout will be required for the Phase I of this project.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

# C:	File