April 1, 2014

Richard J. Berry, Mayor

Glenn Broughton, PE

Bohannan Huston, Inc.

7500 Jefferson NE, Courtyard I

Albuquerque, New Mexico  87113

RE:	ACE Leadership High School  -  1225 Sawmill Road NW		 File:  J13-D099

Drainage Management Plan and Grading Plan for

Building Permit, SO-19 and Work Order		   PE Stamp: 3-11-2014

Dear Mr. Broughton:

Based upon the information provided in your submittal received 3/11/14, the subject Grading and Drainage Plan cannot be approved for Building Permit, SO-19 or Work Order.

Please address the following items for approval:

- The DMP sheet should include a location map (J13) and applicable FIRM map, identifying the Flood Zone applicable to this site.

- Clarify that the impervious areas used in sizing the ponds includes the Gravel roadway surfaces.  If not, boldly note on the DMP and Grading Plan that hard surfacing of those areas will require reanalysis and possible pond size adjustment.

- What surfacing is proposed on the Cul-de-Sac?  Label if it is in the Work Order.

- What is the typical gravel road section?  - Curb & gutter on sides?

- On the G&D, does the Perimeter Retaining/Screen wall prevent cross lot drainage?

- How does the SE entrance tie to Sawmill Road?

- How do you know the invert elevation on the SD Manhole full of dirt?

- Label all items to be built by Work Order, and reference the CPN.

- The SO-19 notes will not be applicable, since the work on Sawmill is in WO.

Since the disturbed area on this site exceeds 1.0 acre, an Erosion and Sediment Control (ESC) Plan, prepared by a NM PE and approved by the City’s Stormwater Engineer, will be required for this site, prior to Hydrology approval of a Building Permit or Work Order.

If you have questions, please email me or telephone 505-924-3994.

Sincerely,

Gregory R. Olson, P.E.

Senior Engineer

Development and Building Services

Orig:	Drainage file:  J13/D099

c.pdf	Addressee via Email  GBroughton@BHInc.com