August 20, 2013

Scott McGee, PE

9700 Tanoan Drive NE

Albuquerque, NM 87104

Re:	Bob’s Burgers, West Central/46th Street, Grading and Drainage Plan

Engineer’s Stamp dated 07-30-2013 (K-12/D032)

Dear Mr. McGee,

Based upon the information provided in your submittal received 08-02-13, the above referenced plan is approved for Site Development for Building Permit.  However, prior to Building Permit approval the following comments will need to be addressed:

- Both proposed curb penetrations need to reference City Standard Drawing #2235. The SO-19 standard notes need to be added to the grading plan.

- Raise the grades south side of the warehouse to create positive flow to the front.

- Provide additional spot elevations along at the sidewalk connection for the ADA path.

- Provide pond calculations for each of the proposed water harvesting ponds.

- Provide top-of-pond and bottom-of-pond elevations for the ponds along with flow calculations and capacity for the two pipe penetrations along Central Ave. Runoff will not be allowed to drain over the sidewalk.

- Are the sidewalks on the plan proposed or existing?

- The trash enclosure will need to show a drain connection to the sanitary sewer system. Provide additional spot elevations at the corners of the enclosure.

- The driveways which are not being used should be removed and new curb and gutter and sidewalk should be constructed.

If you have any questions please call me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development Review Services

C: email