Eugenio E. Valdez, P.E.

Wilson & Company, Inc.

4900 Lang Ave. NE

Albuquerque, NM 87109

Re:	Lincoln Complex, Building M Renovation

Drainage Report/Grading and Drainage Plan

Engineer’s Stamp Date 7-31-2015 (K15/D047B)

Dear Mr. Valdez,

Based upon the information provided in your submittal received 7/17/2015 and 8/3/2015, the above referenced report cannot be approved until the following comments are addressed:

- Please stamp the drainage report.

- Drainage report references flow numbers based on the 100yr/24hr storm.  Please make sure all the flow calculations are based on the 100yr/6hr storm and volume calculations are based on the 100yr/24hr storm.  The runoff calculations for the 100yr/6hr storm are using Type 2 Rainfall.  Summary tables should indicate the 100yr/6hr storm for flows and 100yr/24hr storm for volumes.

- Provide an exhibit that clearly shows the pipe numbers and inlets number shown Table 4 & 5, Sheet 9 of the drainage report.

- First flush volume (0.34” x Impervious Area) must be provided for the new constructions and all the areas that are being reconstructed.

- Please provide all the sheets that are being referenced for details on the grading plans.

- An Erosion and Sediment Control Plan (ESC) submittal is also required for building permit approval.  Please submit an ESC plan including a submittal sheet to Curtis Cherne for review and approval.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

City Engineer, Planning Dept.

Development and Building Services

C:	File