October 30, 2008

Jeffrey G. Mortensen, P.E.

High Mesa Consulting Group

6010-B Midway Park Blvd. NE

Albuquerque, NM 87109

RE:	Highland High School – Lecture Hall Addition           Drain File:  K17 / D021 C

Drainage and Grading Plans for Building Permit	     (P.E. Stamp  10/20/2008)

Dear Mr. Mortensen:

Based upon the information provided in your submittal received 10/20/08, the above referenced Drainage and Grading Plans are approved for Building Permit.

(Note: It appears that there may be an existing roof drain connection from the North side of old Figge Hall to the 10” Private Storm Drain.  Either the demolition project or this construction plan should address capping those lines to avoid sediment entering the Private Storm Drain system.)

Please attach a copy of this approved plan to the Building Permit plan sets prior to requesting sign-off  by the Hydrology Section.

Prior to Certificate of Occupancy approval, an Engineer’s Certification of compliance with this plan is required per the DPM.

If I can be of further assistance, please feel free to contact me at 924-3981.

Sincerely,

Gregory R. Olson, P.E.

Hydrology Section

XC:	Brad Bingham, COA/Hydrology

Drainage file:  K17-D021 C