August 14, 2012

Reza Afaghpour, P.E.

SBS Construction & Engineering, LLC.

P.O. Box 10264

Albuquerque, NM 87184

Re:	Fourplex for Ahmet Tiryaki, 509 Valencia Dr. SE, Grading and Drainage Plan, Engineer’s Stamp dated 08-01-12 (L-18/D078)

Dear Mr. Afaghpour,

Based upon the information provided in your submittal received 08-01-12, the above referenced plan cannot be approved for Building Permit until the following comments are addressed:

- Please correct the proposed conditions of the drainage management plan to state that the ponds will detain “265 cf” of flow instead of plus or minus. Provide pond calculations demonstrating how this is accomplished.

- Show all ponding areas on the plan.

- The waterblock along Valencia Drive appears to be inadequate.

- Provide additional spot elevations along the southern sidewalk since curb will be flush.

- Include additional spot elevations along the northern boundary line to the east of the proposed retaining wall/fence.

- The plan shows both a retaining wall and a 6 foot high fence in the same locations. Please clarify this in the legend or in a detail drawing on the plan.

- The top-of-sidewalk, flowline, and top-of-curb elevations along Valencia Drive should be provided on the plan.

- The last sentence under the “Proposed Conditions and On-Site Drainage Management Plan” heading is illegible and unclear. Charleston Street is not within the vicinity of this drainage plan.

If you have any questions, you can contact me at 924-3994.

Sincerely,

Greg Olsen, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

C:	Email