July 17, 2012

James D. Hughes, P.E.

Mark Goodwin & Associates, PA

P.O. Box 90606

Albuquerque, NM 87199

Re:	Sunport Property Utilities Grading and Drainage Plan, Tract 22 & 23

Engineer’s Stamp Dated 6-7-2012 (M-14/D034)

Dear Mr. Hughes,

Based upon the information provided in your submittal dated 6-20-2012, the above referenced grading and drainage plan cannot be approved for Grading Permit until the following comments are addressed:

- AMAFCA approval is required for discharging into the Southern Diversion

Channel.

- A floodplain permit must be obtained for grading to take place in Basins 105 and

108.

- Provide runoff calculations for each of the basins.

- It appears Basin 103 flows directly into 104 through a 36-inch CMP underneath

Edmund Street and not around the basin to the north as stated in the plan.

- A street capacity analysis will be needed for Edmund Street to ensure flows are contained from Basins 106C and 106D.

- How are flows directed north along the western property edge to the Airport Arroyo Pond?

- Several A-A sections are noted on the plan, are these all supposed to be the same detail?

- Section B-B as well as many of the basin flows are not clearly visible on the plan.

- The effective floodplain date in the legend should read “9-26-2008”.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Building Services

C:     email