August 23, 2013

David Soule, P.E.

Rio Grande Engineering

P.O. Box 93924

Albuquerque, NM 87199

Re:	Hampton Inn At The Sunport Grading and Drainage Plan

Engineer’s Stamp dated 7-29-13 (M15/D043)

Dear Mr. Soule,

Based upon the information provided in your submittal received 7-29-13, the above referenced Grading Plan can not be approved for building permit based on the following comments:

- Plot the existing contour at a lighter color and proposed contour at darker color. It is hard to see the proposed spot elevations.

- Revised grading plan should be approved by Wilfred Gallegos.

- Trash enclosure is not shown.

- Existing concrete wall along the southerly boundary is not shown on the plan.  Section  A-A is not drawn correctly.

- Section B-B should include the actual footing size for the retaining wall.  How will the retaining wall be constructed?  Construction easement will be required from the property owner to the east.

- Provide top of retaining wall and top of footing elevations.

- At the southwest corner of the project proposed contours extend to the adjacent property.  Construction easement will be required.

- Provide more spot elevations along the alley gutter on the east side of the building.  There might be low spots (by elevation 5081.00) on the east of the building.

- Fix the legend.

- Will there be any clear-sight distance issues with the eastern retaining wall being extended to the NE corner of the property?

- Include the City Benchmark on the plan.

- Show the location of the cobble swale on the grading plan or remove the detail if a swale is not needed.

- Remove the architect’s stamp from the plan.

- Pedestrian connection to public sidewalk is not clearly shown.

If you have any questions, you can contact me at 924-3695.

Sincerely,

Shahab Biazar, P.E.

Senior Engineer, Planning Dept.

Development and Review Services

C:	E-mail